PX500 Series Site Checklist

This document lists requirements for the successful installation of a Quantum PX500 Series product in an equipment rack.  Please note that this list is not exhaustive and may change from time to time as elements are added, deleted or modified. Below is a list of critical product and site elements which should be verified prior to attempting the installation of a Quantum product.

- Receiving Considerations

- Rack Installation Requirements

- Electrical & Network Requirements

- Operating Systems Compatibility

- ISV Software Compatibility

- Connectivity (Fiber Switches, GBICs, HBAs, etc.)

The primary resource for verification of items 4-6 is the SOFTWARE COMPATIBILITY GUIDE located at the following link: http://www.quantum.com/swcompguide.aspx.  Additionally, it can be used to do “what if” configurations dynamically and verify them before proceeding.  If some components are not found using this tool  contact a Quantum Sales representative or reseller to request certification testing.

Unit receiving considerations

PX500 family units are mounted to a wooden pallet for shipment and proper planning should be made for their movement to the installation location.  Movement of the unit on a pallet must be done using a proper pallet jack or lifting device as damage may occur otherwise.  The unit should only be removed from its shipping container at or near the actual installation location.

Incoming Shipping dimensions & weights

| Unit | Length | Width | Height | Weight |
| --- | --- | --- | --- | --- |
| PX502 | 42” | 28” | 28” | 125Lbs (approx) |
| PX506 | 42” | 28” | 36” | 180 Lbs (approx) |
| PX510 | 42” | 28” | 48” | 240 Lbs (approx) |

Rack Installation Requirements

Depth The PX500 Series library mounted in a rack requires a minimum depth of 27 in. (69 cm) and a maximum depth of 36 in. (91 cm) between the front and back mounting rails. Optimum rail to rail depth for the entire PX500 family is 31 in

Height PX502 - 4U (6.75 in./17 cm) of vertical rack space per enclosure PX506 - 10U (17.25 in./44 cm) of vertical rack space per enclosure PX510 - requires 18U min, 31.5 in. (80 cm) of vertical rack space per enclosure

Weight PX502 - weighs 65 lbs (29 kg) with 2 drives, 2 magazines, and 0 tape cartridges PX506 - weighs 202lbs (92 kg) with 6 drives, 4 magazines, and 0 tape cartridges PX510 - weighs 334 lbs (152 kg) with 10 drives, 10 magazines, and 0 tape cartridges

| Electrical & Environmental Requirements | Yes | No |
| --- | --- | --- |
| Has the equipment location/arrangement been planned? (power source/host/cabling) |  |  |
| Is emergency power-off capability provided and accessible? |  |  |
| Is the power disconnect (breaker panel or bypass switch) located within sight of the PX500 Series system? (This is a National Electric Code requirement). |  |  |
| Are the temperature, humidity, and airborne contamination at the installation site controlled? |  |  |
| Is there an available IP address for the PX500 Series system, it is required to allow for management of the device on the customers network? |  |  |

Use this area to track your configuration, the information may prove valuable to your installer

## Operating System Version & Patches

| Server Number | Operating System | Version | Patches |
| --- | --- | --- | --- |
| 1. |  |  |  |
| 2. |  |  |  |
| 3. |  |  |  |
| 4. |  |  |  |

ISV Software

| Product Name | Version | Patches | Options |
| --- | --- | --- | --- |

## Interface Host Bus Adapters

| Product Name | Model Name and Driver Revision | Server (Host or Client) | Connection Type |
| --- | --- | --- | --- |

## GBIC Information

| Product Name | Model Name | Specify: Long Wave, Short Wave, Optical or Copper |
| --- | --- | --- |

## Fibre Channel Switch

| Product Name | Model Name | Switch or Hub | Firmware Revision |
| --- | --- | --- | --- |
| Hard or Soft Zoning? |
| Single HBA Zoning? |

Additional copies of this Site Checklist can be obtained from the following link

http://www.quantum.com/ServiceandSupport/SoftwareandDocumentationDownloads/PX500