## Slide 1
August 21, 2015
LATTUS PERFORMANCE
Enrique Lopez-Pineda

## Slide 2: Lattus Performance
Methodologies
  Objectives
  Performance configuration features
  Network evaluation
  Lattus configuration parameters
  StorNext configuration
Performance data
  Performance tests
  Data available from Performance Engineering group

## Slide 3: Performance Methodologies
Objectives and configuration

## Slide 4: Performance Methodologies
Performance Testing Objectives
  Aggregate PUT/GET performance
  Single and multiple stream (series) performance
  Throughput performance
Performance configuration features
  Transmission packets (MTU)
    Set MTU to 9000 (jumbo frames)
      MDC, DDMs, Lattus controllers and on interconnect switch
        Note: for interconnect switch use MTU=9216
  Network transfer protocol (HTTP/HTTPS)

## Slide 5: Performance Methodologies (cont.)
Performance configuration features (cont.)
  Client daemons (Lattus)
    4 client daemons gives better performance (uses more memory)
  Data movers (DDMs) - StorNext
    Feature to distribute data movement operations to client machines to improve the overall throughput of data movement
    Evaluate the following to determine number of DDMs for best performance:
      Number of storage nodes
      Number of client daemons
  System Parameters
    Update to following in /usr/adic/TSM/config/fs_sysparm file
      MAX_FILES_PER_CLUSTER=350;
        Allows for better distribution of I/O requests across all data movers
        Assuming Lattus Object Storage configured with 48 streams per controller

## Slide 6: Performance Methodologies (cont.)
Network Evaluation
  Use 10G connection between MDC and Lattus
  Raw network throughput (MDC to Lattus controller)
    ttcp utility
Lattus Tuning parameters
  DSS storage policy
    Safety strategy should be RepairSpread & DynamicSafety
    C5 6-node: storage width: 16 storage safety: 4
    C10 20-node: storage width: 20 storage safety: 4
  Update Lattus configuration files based on values for maximum throughput as stated in Installation Guide
    Client daemon
    Storage daemon
    Maintenance agent

## Slide 7: Performance Methodologies (cont.)
StorNext Configuration (MDC and DDMs)
  Filesystem parameters
    Parameters generally modified from defaults for performance as follows
      Journal size: 256 MB
      ASR: 1 GB
      Buffer cache size: 4 GB
      Inode cache size: 512 KB
      Stripe groups: sg0: Metadata/Journal
              sg1: Data
      Stripe breadth: sg0: 256 MB
              sg1: [RAID layout dependent: 256kb x #data disks per LUN]
              example: QXS5600: RAID6 12+2 == 256 x 12 = 3 GB]
  DDM setup
    Use primary and secondary MDC nodes as default DDMs
    Additional clients can be setup for more DDMs (recommend 2 clients – 4 DDMs)

## Slide 8: Performance Tests
Test characteristics and objectives

## Slide 9: Performance Tests
Baseline Throughput Test (HTTP PUT/GET test)
  Run burn-in script as provided by Amplidata to measure GET and PUT HTTP performance between the controller nodes and the storage
    For AXR: python-PUT-GET-standalone.sh
    For S3: s3_perf_text.py
  Test should be run from MDC as well as from main controller node
  Does not involve StorNext
  Perform multiple series runs of 1 GiB objects
    Case 1: 1 controller with 16 series
    Case 2: 1 controller with 48 series
    Case 3: 3 controllers with 16 series per controller
    Case 4: 3 controllers with 48 series per controller
  Results: Aggregate GiB/sec performance

## Slide 10: Performance Tests (cont.)
Large file aggregate store and retrieve performance
  Measure aggregate multi-stream performance for large (100 GB) files
    Uses fsstore and fsretrieve commands
    Runs for 16 and 18 streams
    Data generated using lmdd
    Results: Aggregate MBytes/sec performance

## Slide 11: Performance Tests (cont.)
Small file Storage Manager throughput tests
  Use SM policy to store and retrieve files
  Uses vidio tool to create 50000 DPX 4K frame files (about 50 MB size per file)
    vidio is a video frame producer consumer performance test (part of SN distribution)
  Measure throughput performance of SM store operations for DPX 4K file.
    Two cases
      SM policy active as files are being created
      SM policy locked while files are created; policy unlocked once all files are created
  Measure throughput performance of SM retrieve operations for DPX 4K files
  Results: Mbytes/sec rate for stores and for retrieves

## Slide 12: Performance Data
Current QA Engineering results

## Slide 13: Baseline Throughput Results Lattus C5 6 S20 Nodes, AXR, HTTPS
Main controller - AXR Results (Lattus 3.4.3) Lattus C5 6 S20 Node [POLICY 16/4] |  |  | 
# Controllers | # series/controller | PUT MBytes/sec | GET MBytes/sec
1 | 16 | 434 | 715
1 | 48 | 443 | 729
3 | 16 | 696 | 972
3 | 48 | 725 | 989

## Slide 14: Baseline Throughput Results Lattus C5 6 S20 Nodes, AXR, HTTPS
MDC- AXR Results (Lattus 3.4.3) Lattus C5 6 S20 Node [POLICY 16/4] |  |  | 
# Controllers | # series/controller | PUT MBytes/sec | GET MBytes/sec
1 | 16 | 426 | 848
1 | 48 | 450 | 870
3 | 16 | 682 | 957
3 | 48 | 720 | 986

## Slide 15: Baseline Throughput Results Lattus C10 20 S30 Nodes, S3, HTTPS
Main controller – S3 Results (Lattus 3.6.0) Lattus C10 20 S30 Node [POLICY 20/4] |  |  | 
# Controllers | # series/controller | PUT MBytes/sec | GET MBytes/sec
1 | 16 | 1188 | 1314
1 | 48 | 1135 | 1496
3 | 16 | 2861 | 2571
3 | 48 | 2717 | 2948

## Slide 16: Baseline Throughput Results Lattus C10 20 S30 Nodes, S3, HTTPS
MDC- S3 Results (Lattus 3.6.0) Lattus C10 20 S30 Node [POLICY 20/4] |  |  | 
# Controllers | # series/controller | PUT MBytes/sec | GET MBytes/sec
1 | 16 | 1337 | 1145
1 | 48 | 1191 | 1488
3 | 16 | 1607 | 1521
3 | 48 | 1614 | 1667

## Slide 17: Large file fsstore results Lattus C5 6 S20 Nodes, AXR, HTTPS
fsstore results (Lattus 3.4.3) Lattus C5 6 S20 Node [POLICY 16/4, AXR, HTTPS] |  |  | 
DDMs | Files | Mbytes/sec (2 CDs) | Mbytes/sec (4CDs)
2 | 16 | 686 | 690
2 | 18 | 716 | 706
4 | 16 | 650 | 722
4 | 18 | 702 | 739

## Slide 18: Large file fsretrieve results Lattus C5 6 S20 Nodes, AXR, HTTPS
fsretrieve results (Lattus 3.4.3) Lattus C5 6 S20 Node [POLICY 16/4, AXR, HTTPS] |  |  | 
DDMs | Files | Mbytes/sec (2 CDs) | Mbytes/sec (4CDs)
2 | 16 | 911 | 902
2 | 18 | 955 | 951
4 | 16 | 957 | 910
4 | 18 | 964 | 959

## Slide 19: Large file fsstore results Lattus C10 20 S30 Nodes, S3, HTTP
fsstore results (Lattus 3.6.0) Lattus C10 20 S30 Node [POLICY 20/4, S3, HTTP] |  |  | 
DDMs | Files | Mbytes/sec (2 CDs) | Mbytes/sec (4CDs)
2 | 16 | 1930 | 2403
2 | 18 | 2044 | 2489
4 | 16 | 1889 | 2243
4 | 18 | 2062 | 2341

## Slide 20: Large file fsretrieve results Lattus C10 20 S30 Nodes, S3, HTTP
fsretrieve results (Lattus 3.6.0) Lattus C10 20 S30 Node [POLICY 20/4, S3, HTTP] |  |  | 
DDMs | Files | Mbytes/sec (2 CDs) | Mbytes/sec (4CDs)
2 | 16 | 2109 | 2236
2 | 18 | 1777 | 2464
4 | 16 | 3295 | 3142
4 | 18 | 2912 | 3059

## Slide 21: Large file fsstore results Lattus C10 20 S30 Nodes, S3, HTTPS
fsstore results (Lattus 3.6.0) Lattus C10 20 S30 Node [POLICY 20/4, S3, HTTPS] |  |  | 
DDMs | Files | Mbytes/sec (2 CDs) | Mbytes/sec (4CDs)
2 | 16 | 1689 | 1730
2 | 18 | 1384 | 1369
4 | 16 | NA | 1081
4 | 18 | NA | 1240

## Slide 22: Large file fsretrieve results Lattus C10 20 S30 Nodes, S3, HTTPS
fsretrieve results (Lattus 3.6.0) Lattus C10 20 S30 Node [POLICY 20/4, S3, HTTPS] |  |  | 
DDMs | Files | Mbytes/sec (2 CDs) | Mbytes/sec (4CDs)
2 | 16 | 1085 | 1096
2 | 18 | 1223 | 1223
4 | 16 | NA | 934
4 | 18 | NA | 1046

## Slide 23: Storage Manager Throughput Results Lattus C5 6 S20 Nodes, AXR, HTTPS FA4K frames, 50K files
DDMs | Client Daemons | Concurrent Ingest | Completed Ingest | Retrieve
2 | 2 | 615 | 629 | 956
2 | 4 | 702 | 711 | 961
4 | 2 | 614 | 615 | 973
4 | 4 | 709 | 738 | 987

## Slide 24: Storage Manager Throughput Results Lattus C10 20 S30 Nodes, S3, HTTP FA4K frames, 50K files
DDMs | Client Daemons | Concurrent Ingest | Completed Ingest | Retrieve
2 | 2 | 1541 | 1510 | 1138
2 | 4 | 1619 | 1514 | 1156
4 | 2 | 1602 | 1615 | 1207
4 | 4 | 1629 | 1787 | 1265

## Slide 25: Storage Manager Throughput Results Lattus C10 20 S30 Nodes, S3, HTTPS FA4K frames, 50K files
DDMs | Client Daemons | Concurrent Ingest | Completed Ingest | Retrieve
2 | 2 | 1565 | 1698 | 737
2 | 4 | 1559 | 1514 | 825
4 | 2 | NA | NA | NA
4 | 4 | 1616 | 1610 | 942

## Slide 26
For meeting with Quantum, the LARGEST Data Protection and Big Data management specialist in the world.
THANK YOU
© 2015 Quantum Corporation. Company Confidential. Forward-looking information is based upon multiple assumptions and uncertainties, does not necessarily represent the company’s outlook and is for planning purposes only.