## Slide 1
SNFS Performance Analysis and Tuning
SNFS Development Team
7-March-2012

## Slide 2: Performance Analysis Scenarios
Metadata Operations
  Other notable items in the cvlogs
  Tracing high level file systems operations
Server side cvfsdb command
  Used to investigate SNFS metadata
Cvdb options
Client cvdb traces
  Tracing high level file system operations
  Performance tracing

## Slide 3: Looking a Metadata Performance
What operations are exercising the metadata paths?
  Everything that is not going through the data path must go through the metadata
What components are involved in the metadata path?
  Metadata Controller
  Metadata Disks
  Journal Disk
  FSM Process
  Metadata Network
  SNFS Client

## Slide 4: Where to start…
What are some examples of metadata performance issues?
  Running ‘ls –l’ is has gotten very slow
  The system isn’t as responsive
  Running ‘rm’ or ‘rm –r’ feels slow

## Slide 5: My ‘ls –l’ is slow…
Let’s look at an instance where a user complains that running ‘ls –l’ on a directory is slow
A couple quick questions to ask
  Is the performance problem seen in one directory or all directories?
  When did the issue start?
  What does the directory look like?
    How large is the directory
    How many users access it at the same time
    Has it grown recently

## Slide 6: My ‘ls –l’ is slow…
For starters it helps to break down what an ‘ls –l’ is doing inside the file system
This command will be running a readdir operation followed by a stat on each file and directory
  In this case, in interesting question is whether an ‘ls’ is also slow. If it is, the ReadDir operation is likely at the core of the issue. If not, then the stat operations may behaving an impact.
The FSM hourly stats are a good starting point in the investigation
FSM stats can be found in the qustat logs
  /usr/cvfs/qustat/FSM/<fsname>/<server>/
In this case, we will start looking at the VOP traces which represent the high level file system operations

## Slide 7: My ‘ls –l’ is slow…
When looking at hourly stats, find the time period which exhibited the performance issue
In the qustat logs we will look at VOPS
  Starting with “VOP Read DirV2”
  # NAME,TYP,COUNT,MIN,MAX,TOT/LVL,AVG
  VOP Read DirV2,TIM,377783,0,238367,1062358171,2812
  In this case there were 377,783 ReadDir requests over the course of the hour
  The Min and Max times for ReadDir operations were 0 microseconds and 238,367 microseconds respectively
  The average response time was 2,812 microseconds
In this case the FSM stats appear to be reasonable. But we can look for trends to verify that

## Slide 8: Looking at trends
Let’s look at how the ReadDir operation has behaved over time
Using tools like grep or perl we can pull out some trends
  # NAME,TYP,COUNT,MIN,MAX,TOT/LVL,AVG
  VOP Read DirV2,TIM,358339,0,216499,1256261500,4863
  VOP Read DirV2,TIM,331808,0,301828,1096549204,4730
  VOP Read DirV2,TIM,346714,0,207206,1223235546,4958
  VOP Read DirV2,TIM,326206,0,206097,1050113428,4642
  VOP Read DirV2,TIM,337279,0,190037,1191142885,5020
  VOP Read DirV2,TIM,366203,0,196760,1238128009,4651
  VOP Read DirV2,TIM,270037,0,176581,734174025,4318
  VOP Read DirV2,TIM,277707,0,189693,816662549,4596
  This is just a small sample, but if the numbers looked similar, and these numbers covered time periods that saw no problems it’s possible that the issue is isolated to a single client and not seen across the cluster

## Slide 9: My ‘ls –l’ is slow (part two)…
What if the numbers looked different?
Going back to the qustat logs we will look at VOPS again
  Back to “VOP Read DirV2”
  # NAME,TYP,COUNT,MIN,MAX,TOT/LVL,AVG
  VOP Read DirV2,TIM,12377783,0,1238367,1062358171,22812
  Now we see 12,377,783 ReadDir requests over the course of the hour
  The Min and Max times for ReadDir operations were 0 microseconds and 1,238,367 microseconds respectively
  The average response time was 22,812 microseconds
12 Million ReadDir requests over the course of an hour seems a bit high, let’s take a look.

## Slide 10: My ‘ls –l’ is slow (part two)…
If the counts before the problem started look similar to our original example, ~300,000 ReadDir requests per hour, then we’ll want to figure out what is triggering the extra requests
The next step is to look at the client specific stats. There is an hourly VOP counter for each connected client
# Table,154,Name,VOPS: Client prod-cifs1.domain.com
# Last Reset, Secs, 3600, time_t, 1331589600, date, 2012-03-07 17:00:00 CDT
# NAME,TYP,COUNT,MIN,MAX,TOT/LVL,AVG
…
VOP DirAttr V2,TIM,12123323,2402,1254560,1457176,20262
In this case we see that one client is sending the majority of the additional ReadDir request
Next we look on the system to determine which user or process is causing the extra load

## Slide 11: My ‘ls –l’ is slow (part three)…
Let’s look at a new scenerio
Back in the qustat logs we will look at VOPS
  Starting with “VOP Read DirV2”
  # NAME,TYP,COUNT,MIN,MAX,TOT/LVL,AVG
  VOP Read DirV2,TIM,377783,24232,4338367,1062358171,45812
  In this case there were 377,783 ReadDir requests, just as there were in the original example
  However, now the Min and Max times for ReadDir operations were 24,323 microseconds and 4,338,367 microseconds respectively
  The average response time was 45,812 microseconds
In this case the volume of ReadDir requests is probably reasonable, but the calls are taking much longer to complete

## Slide 12: My ‘ls –l’ is slow (part three)…
At this point, the disks would be a good place to look
Back over to the qustat logs we will look at PIO
  # Table,9,Name,Phys IO: HBA 1 LUN 0 CvfsDisk_LsiHome_Meta10
  # Last Reset, Secs, 3600, time_t, 1331589600, date, 2012-03-12 17:00:00 CDT
  # NAME,TYP,COUNT,MIN,MAX,TOT/LVL,AVG
  PIO Read Normal,TIM,65577,0,1289520,186169807,20839
  PIO Read Phys,TIM,65577,0,1 128899,152035612,2318
  PIO Write Norml,TIM,1582,119,21171,797470,504
  PIO Write HiPri,TIM,2901,52,2299,744628,257
  PIO Write Phys,TIM,4483,49,8599,1107800,247
  A ReadDir operation is going to go through the “PIO Read Normal” path
  The request times here are > 1 second. That should be looked at next

## Slide 13: The PIO stats
The PIO stats measure the metadata and journal read an write timings
What do the PIO counters mean
  PIO Read Normal - Standard Metadata Reads
  PIO Read Phys - Device Read Requests
  PIO Write Normal - Standard Metadata Writes
  PIO Write HiPri - Journal Updates
  PIO Write Phys - Device Write Requests
High I/O latency could be due to hardware issues like drive errors or RAID rebuilds
Overutilization of a drive, or very high levels of random I/O can also result in latency

## Slide 14: I/O latency
There are a couple tools that can help when looking at high I/O latency
iostat – This tool will give some insight into what a device is doing from the perspective of the I/O
  High utilization counts through iostat tend to point towards disk thrashing
RAID monitoring tools
  This can show more detailed characteristics of the storage
Depending on the nature of the issue there are a number of areas to look at
  Is the RAID tuned and operating properly (is caching enabled? Is the controller battery good? Are there any failed drives?)
  Are all of the SAN connections solid?
  Are the applications utilizing the file system efficiently?
  Is the FSM BufferCache and InodeCache optimal? Does increasing the value help?

## Slide 15: FSM caches
The primary caches in the FSM are the Inode Cache and the Buffer Cache
  The defaults for these values are on the low side
In environments containing directories with tens of thousands of files or more, increasing the inodeCacheSize is recommended
  Increasing inodeCacheSize consumes about 1k per additional entry
It is also recommended that the BufferCacheSize be increased in environments with large directories or large client counts
  Some environments have seen notable gains when increasing the BufferCacheSize to 128MB and larger

## Slide 16: Client Performance Analysis
What are the expectations of the SNFS client?
What are capabilities of the storage?
  Will the SAN and storage infrastructure support the requirements?
  What does the aggregate utilization look like?
Is file fragmentation a factor?
Is random I/O a factor?
Is unaligned I/O a factor?

## Slide 17: Capabilities of the environment
Some questions on the performance expectations and capabilities
  What are the capabilities of the storage environment? Will the storage support the overall load that is being put on the environment?
  Are there throughput requirements or I/O latency requirements?
  What does the storage utilization look like? Are there tools to monitor the RAID devices?
Is the client provisioned to support the expected throughput?
  CPU, memory, HBA

## Slide 18: Checking for fragmentation
When looking at I/O performance problems, fragmentation should be considered
Running the snfsdefrag -e command will show how fragmented a file is
# snfsdefrag -e snapshot-20120207125416.tar.gz
snapshot-20120207125416.tar.gz:
# group frbase fsbase fsend kbytes depth
0 3 0x0 0x4c6c910 0x4c6cb7c 9936 10
1 3 0x9b4000 0x493dfbd 0x493e291 11600 10
The number of fragments as well as the average extent size are important in assessing the effects of fragmentation
The smaller the extents the higher the metadata overhead involved in accessing file data

## Slide 19: What causes fragmentation
There are a handful of reasons that a file might be fragmented
  The I/O patterns result in fragmentation
    Slow writing
    Random writes
  The free block pool is fragmented
    This is generally more prevalent on systems which are close to capacity

## Slide 20: Investigating I/O patterns
The “cvdb perf” traces can show I/O patterns
In this case the “rwcvp” line shows the offset and length of the I/O
  Uio_offset is the offset
  Uio_resid is the length
  To find common I/O requests, the second field in the header (8487) is the pid of the requesting process.
<1:8487:219.634911> PERF: rwcvp: cvp 0xffff88005bb7f080 rw 0x1 uio_offset 0x9c36000 uio_resid 0x2000 cursize 0x9c36000 fileflags 0xc001 ioflags 0x0
<1:8487:219.634918> PERF:[280102] Device Write Start: off 0x9c36000 len 0x2000 ino 0x214196 unit 1
<1:2031:219.635109> PERF:[280102] Device Write Completed: 41 MB/s (189us) off 0x9c36000 len 0x2000 ino 0x214196 unit 1
<1:8487:219.635118> PERF: VFS Write EofDmaAlgn 37 MB/s (209us) off 0x9c36000 len 0x2000 ino 0x214196

## Slide 21: Investigating I/O patterns
Following a processes I/O requests over time will show how sequential or random the I/O is
<1:8487:219.634911> PERF: rwcvp: cvp 0xffff88005bb7f080 rw 0x1 uio_offset 0x9c36000 uio_resid 0x2000 cursize 0x9c36000 fileflags 0xc001 ioflags 0x0
<1:8487:219.634918> PERF:[280102] Device Write Start: off 0x9c36000 len 0x2000 ino 0x214196 unit 1
<1:2031:219.635109> PERF:[280102] Device Write Completed: 41 MB/s (189us) off 0x9c36000 len 0x2000 ino 0x214196 unit 1
<1:8487:219.635118> PERF: VFS Write EofDmaAlgn 37 MB/s (209us) off 0x9c36000 len 0x2000 ino 0x214196

## Slide 22: Investigating I/O alignment
The offset and size of I/Os can also be used to indicate the alignment of the I/O requests
<1:8487:219.634911> PERF: rwcvp: cvp 0xffff88005bb7f080 rw 0x1 uio_offset 0x9c36000 uio_resid 0x2000 cursize 0x9c36000 fileflags 0xc001 ioflags 0x0
<1:8487:219.634918> PERF:[280102] Device Write Start: off 0x9c36000 len 0x2000 ino 0x214196 unit 1
<1:2031:219.635109> PERF:[280102] Device Write Completed: 41 MB/s (189us) off 0x9c36000 len 0x2000 ino 0x214196 unit 1
<1:8487:219.635118> PERF: VFS Write EofDmaAlgn 37 MB/s (209us) off 0x9c36000 len 0x2000 ino 0x214196

## Slide 23
Questions