## Slide 1: SN Appliance and Platform
7/17/2013

## Slide 2: 4.7 Changes
OS upgrade for the M330 to CentOS 5.9
  Improved DM-MP driver support in the newer kernel
Upgrade changes for post 4.7 releases
New NetApp controller firmware for all platforms
M330 now supports a dual-FC expansion card option like the M440
Updated HW component firmware for several components
Hot spare replacement service menu option

## Slide 3: Hot Spare Replacement
New option to replace a failed hot spare drive
  *** Service Setup Array Menu ***
  0) Save Array configurations - Save all Array configs before modifications.
  1) Rescan for Arrays - Rescan the system for the connected NetApp array.
  2) Upgrade Array Firmware >>> - Download new Array Controller Firmware or NVSRAM.
  3) Display Array BBU status - Display the status and age of the array BBU.
  4) Reset Array BBU date - Reset the day counter for a replaced array BBU.
  5) Replace Array controller - Replace an array controller.
  6) Replace Hot Spare Drive - Replace a failed hot spare drive.
  7) Manufacturing >>> - Tools for Manufacturing.
  Your Choice ('q' to Exit this Menu):

## Slide 4: Upgrade changes
4.7 code base now support standalone platform-only and StorNext-only .fw upgrades
4.7 release will still be a combined platform and StorNext .fw image but we now have more flexibility for future LCR upgrades if needed
4.7 combined .fw upgrade will actually consist of 2 .fw files (part 1of2 and part 2of2). Both will need to be uploaded to the GUI and activation of either file will install both uploaded files. This was needed since the size of the upgrade is > 2GB.

## Slide 5: Upgrade Process Flow
M-Series
  Upon activation, GUI calls /opt/DXi/Install_New_Image script on the primary node, passing in the full path to the upgrade file
  Install_New_Image does a checksum and version verification on the uploaded .fw files by calling the Verify_New_Image script
  Install_New_Image verifies that all the required .fw file parts were uploaded and matching. It also runs a verification of matching API versions between the SN GUI and the platform
  It then launches the Upgrade script from the extracted .fw in the background on the primary node
  The GUI then performs the same sequence on the secondary node

## Slide 6: Upgrade Process Flow
M-Series cont’d
  The Upgrade script is a dual purpose script. When called from the Install_New_Image script, the Upgrade script performs some initial synchronization between the primary and secondary nodes before the system is rebooted. The Upgrade script is also a boot-time RC script and it enables itself before rebooting on each node so that the upgrade can continue during the reboot.
  The secondary node uninstalls StorNext before the reboot. The primary will not do its reboot until the secondary finishes its uninstall so that we keep the two nodes in sync with their software versions.

## Slide 7: Upgrade Process Flow
M-Series cont’d
  During the boot the Upgrade script calls UpgradeBase.sh to perform the majority of the software updates.
  UpgradeBase.sh performs many steps and software updates including, FW bundles, OS, Quantum Platform RPMs, and StorNext bundle.
  The StorNext bundle is upgraded on the primary node and fresh installed on the secondary node.

## Slide 8: Upgrade Process Flow
M-Series cont’d
  Once all the packages are upgraded/installed, the nodes are rebooted independently
  During this reboot, any required updates to FW on HW components will be done automatically early in the boot by the fw_bundle boot script. This can result in subsequent reboots since many of the HW components require reboots after the FW is flashed.
  For 4.7, the NetApp array firmware will also be autoleveled during the boot from the primary node. This will add a couple extra minutes to the upgrade but no extra reboot is required.

## Slide 9: Upgrade Process Flow
M-Series cont’d
  After the nodes have completed the bootup, HA conversion of the secondary node is required from the GUI, followed by a startup of Storage Manager. This should complete the upgrade and the system should be back online.
  Check for any new RAS tickets if something goes wrong during the upgrade.
  All upgrade logs are located in /var/log/DXi/upgrades/ and are timestamped.
  For 5.0, I am going to consolidate the log files to a single file for easier debugging

## Slide 10: Upgrade Process Flow
M-Series cont’d
  What to do if an upgrade fails on one of the nodes?
    In most cases, when an upgrade fails (ie. the StorNext bundle aborts during install.stornext), the upgrade on that node will stop at that point and log a RAS ticket. Manual intervention is now required.
    Check the log files for the error condition that caused the failure. In some cases, (ie. failure due to a timeout waiting for a slow disk), a retry of the upgrade is all that is needed to complete the upgrade successfully.
    When an upgrade aborts, all the extracted .fw upgrade files will be left in /scratch/upgrade on the node. This allows the option to copy the Upgrade script back into /etc/init.d/ and then re-enable the script to run on the next boot using “chkconfig Upgrade on”. Rebooting the machine will cause the upgrade to run again. It will skip over packages that are already upgraded. This should only be done after proper analysis of the failure in the log files.

## Slide 11: Questions/Discussions?
Just fyi, here is a draft document that goes into more detail of the upgrade process :
StorNext_4.7#New_Features-Platform